{"text_format":"3","workbook":"xlsx","n_sheets":8,"sheets":["填表说明","重点排污单位环境信息公开表","烟气检测数据汇总","烟气重金属检测数据汇总","废水检测数据汇总","飞灰检测数据汇总","炉渣热酌减率数据汇总","二噁英数据汇总"],"read":"whole","date_system":"1900"}

{"sheet":"填表说明","index":0,"n_rows":13,"n_cols":1,"rows_kept":13}
["关于运营项目公司环保信息公示资料准备的情况说明"]
["一、根据《企业事业单位环境信息公开办法》、《生活垃圾焚烧污染控制标准》(GB18485-2014)要求，所有运营的垃圾焚烧项目公司都需进行网上公示。"]
["二、资料准备："]
["1、重点排污单位环境信息公开表"]
["2、16年环保监测计划。若项目公司没有监测计划，以海安监测计划为模板，结合本企业的环评、《生活垃圾焚烧污染控制标准》(GB18485-2014)的要求编制监测计划，并到当地环保部门备案。"]
["3、16年1-7月环保检测数据汇总表（烟气检测数据汇总、烟气重金属检测数据汇总、废水检测数据汇总、飞灰检测数据汇总、炉渣热酌减率数据汇总、二噁英数据汇总）"]
["4、16年1-7月第三方检测报告（按月份进行整理归档）"]
["三、资料提交："]
["1、《重点排污单位环境信息公开表》需提供纸质版和电子版，纸质版需项目公司负责人签字确认；"]
["2、《16年环保监测计划》需提供纸质版和电子版，纸质版需项目公司负责人签字确认；"]
["3、《16年1-7月环保检测数据汇总表》需提供纸质版和电子版，纸质版需项目公司负责人签字确认；"]
["4、《16年1-7月第三方检测报告》只需提供电子版。"]
["四、请各项目公司在2016年8月31日前，按照上述相关要求填写相关表格，同时将所需的纸质版文件邮寄至中国天楹总部林峰。联系人电话：15358703198、短号：69750"]

{"sheet":"重点排污单位环境信息公开表","index":1,"n_rows":46,"n_cols":10,"rows_kept":46,"merged":[[0,1,0,10],[1,1,1,10],[2,1,2,2],[2,3,2,6],[2,7,2,8],[2,9,2,10],[3,1,3,2],[3,3,3,6],[3,7,3,8],[3,9,3,10],[4,1,4,2],[4,3,4,10],[5,1,5,10],[6,1,6,4],[6,5,6,6],[6,7,6,10],[7,1,7,4],[7,5,7,6],[7,7,7,10],[8,1,8,10],[9,1,9,5],[9,6,9,10],[10,1,10,5],[10,6,10,10],[11,1,11,10],[12,1,12,2],[12,4,12,10],[13,1,13,2],[13,4,13,6],[13,7,13,8],[13,9,13,10],[14,1,14,2],[14,4,14,6],[14,7,14,8],[14,9,14,10],[15,1,15,2],[15,4,15,6],[15,7,15,8],[15,9,15,10],[16,1,16,10],[17,1,17,2],[17,4,17,10],[18,1,18,2],[18,4,18,6],[18,7,18,8],[18,9,18,10],[19,1,19,2],[19,4,19,6],[19,7,19,8],[19,9,19,10],[20,1,20,2],[20,4,20,6],[20,7,20,8],[20,9,20,10],[21,1,22,2],[21,4,21,6],[21,7,21,10],[22,4,22,6],[22,7,22,10],[23,1,23,2],[23,4,23,10],[24,1,24,10],[25,1,25,2],[25,4,25,7],[25,8,25,10],[26,1,26,2],[26,4,26,7],[26,8,26,10],[27,1,27,2],[27,4,27,7],[27,8,27,10],[28,1,28,10],[29,1,29,2],[29,4,29,7],[29,8,29,10],[30,1,30,2],[30,4,30,7],[30,8,30,10],[31,1,31,2],[31,4,31,7],[31,8,31,10],[32,1,32,10],[33,1,33,5],[33,6,33,10],[34,1,34,5],[34,6,34,10],[35,1,35,5],[35,6,35,10],[36,1,36,5],[36,6,36,10],[37,1,37,10],[38,1,38,5],[38,6,38,10],[39,1,39,5],[39,6,39,10],[40,1,40,10],[41,1,41,5],[41,6,41,10],[42,1,42,5],[42,6,42,10],[43,1,43,5],[43,6,43,10],[44,1,44,5],[44,6,44,10],[45,1,45,5],[45,6,45,10]]}
[null,"延吉天楹环保能源有限公司环境信息公开表"]
[null,"一、基础信息"]
[null,"单位名称",null,"延吉天楹环保能源有限公司",{"$nulls":3},"法定代表人",null,"严圣军"]
[null,"组织机构代码",null,"912224015944698252",{"$nulls":3},"联系方式",null,15567668557]
[null,"生产地址",null,"吉林省延吉市小营镇小营村"]
[null,"生产经营和管理服务的主要内容、产品及规模"]
[null,"主要内容",{"$nulls":3},"产品",null,"规模"]
[null,"垃圾焚烧发电及蒸汽生产；炉渣及制品销售；",{"$nulls":3},"电能",null,"日焚烧处理800吨生活垃圾，配置2台400吨生活垃圾的焚烧线，1套15MW汽轮发电机组。"]
[null,"二、排污信息"]
[null,"执行的污染物排放标准",{"$nulls":4},"核定的污染物排放量"]
[null,"《生活垃圾焚烧污染控制标准》GB18485-2014，《污水综合排放标准》GB8978-1996，《工业企业厂界环境噪声排放标准》GB12348-2008,《生活垃圾填埋场污染控制标准》GB16889-2008",{"$nulls":4},"吉林省建设项目主要污染物总量控制指标确认书：许可排放量：二氧化硫66t/a、氮氧化物410.7t/a、化学需氧量：5.54t/a、氨氮：0.72t/a."]
[null,"（一）、废水"]
[null,"主要污染物及特征污染物名称",null,null,"化学需氧量、氨氮"]
[null,"排放方式",null,null,"排至污水处理厂",null,null,"排放口数量和分布情况",null,"厂区西侧排放口"]
[null,"排放浓度",null,null,"COD≤500mg/L",null,null,"超标情况",null,"无"]
[null,"执行的污染物排放标准",null,null,"《污水综合排放标准》GB8978-1996三级标准",null,null,"核定的排放总量",null,"COD：5.54t/a； 氨氮：0.72t/a"]
[null,"（二）、废气"]
[null,"主要污染物及特征污染物名称",null,null,"烟尘、二氧化硫、氯化氢、氮氧化物、一氧化碳"]
[null,"排放方式",null,null,"高空达标排放",null,null,"排放口数量和分布情况",null,"1个（2条单独线并一个烟囱内）"]
[null,"排放浓度",null,null,"烟尘≤20mg/m3、HCL≤50mg/m3，SO2≤80mg/m3，NOX≤250mg/m3，CO≤80mg/m3",null,null,"超标情况",null,"无"]
[null,"执行的污染物排放标准",null,null,"《生活垃圾焚烧污染控制标准》（GB18485-2014）",null,null,"核定的排放总量",null,"二氧化硫66t/a、氮氧化物410.7t/a"]
[null,"(三）、固体废物、危险废物情况",null,null,"一般固体废物",null,null,"危险固体废物"]
[{"$nulls":4},"炉渣",null,null,"飞灰、废机油"]
[null,"(四）、固化飞灰去向",null,null,"吉林省延边州龙井市东山垃圾填埋处理场"]
[null,"三、防治污染设施的建设和运行情况"]
[null,"设施名称",null,null,"主要工艺",{"$nulls":3},"验收时间"]
[null,"废水处理设施",null,null,"调节池+UASB（厌氧池）+A/O（硝化反硝化）+超滤+纳滤",{"$nulls":3},"2018-02-05"]
[null,"废气处理设施",null,null,"SNCR+半干法消石灰脱酸+活性炭吸附+布袋除尘",{"$nulls":3},"2018-02-05"]
[null,"四、建设项目环境影响评价情况及环境保护行政许可情况（各项分别填写）"]
[null,"项目名称",null,null,"建设项目环境影响评价批复情况",{"$nulls":3},"文号"]
[null,"延吉市生活垃圾焚烧发电厂项目环境影响报告书",null,null,"已批复",{"$nulls":3},"吉环审字[2013]77号"]
[null,"设施竣工环保验收",null,null,"已验收",{"$nulls":3},"吉环函[2018]129号"]
[null,"五、突发环境事件应急预案"]
[null,"今年来发生的特发环境事件",{"$nulls":4},"无"]
[null,"突发环境事件应急预案颁布实施日期",{"$nulls":4},"2017-05-01"]
[null,"突发环境事件应急预案备案情况",{"$nulls":4},"已于2017年5 月进行了备案"]
[null,"应急预案演练情况",{"$nulls":4},"2018年3月，盐酸泄漏事故应急处理演练"]
[null,"六、环境自行监测方案及其备案情况(2018年）"]
[null,"（一）、环境自行监测方案",{"$nulls":4},"已制定，具体见附件"]
[null,"（二）、环境自行监测方案备案情况",{"$nulls":4},"已于2018年 1月进行了备案"]
[null,"（三）、自行监测结果"]
[null,"废气",{"$nulls":4},"符合要求，具体见附件"]
[null,"废水",{"$nulls":4},"符合要求，具体见附件"]
[null,"固化飞灰",{"$nulls":4},"符合要求，具体见附件"]
[null,"炉渣",{"$nulls":4},"符合要求，具体见附件"]
[null,"二噁英",{"$nulls":4},"符合要求，具体见附件"]

{"sheet":"烟气检测数据汇总","index":2,"n_rows":29,"n_cols":5,"rows_kept":29,"merged":[[0,0,0,4],[1,0,7,0],[8,0,14,0],[15,0,21,0],[22,0,28,0]]}
["延吉天楹环保能源有限公司烟气检测数据汇总"]
["2018年第一季度","检测日期","2018-03-19","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"烟尘",30,"/",3]
[null,"二氧化硫",100,"/",30]
[null,"氮氧化物",300,"/",234]
[null,"氯化氢",60,"/",5]
[null,"一氧化碳",100,"/",9]
["2018年第二季度","检测日期","2018-06-26","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"烟尘",30,3,8]
[null,"二氧化硫",100,60,72]
[null,"氮氧化物",300,245,270]
[null,"氯化氢",60,7,8]
[null,"一氧化碳",100,22,2]
["2018年第三季度","检测日期","2018-09-29","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"烟尘",30,1.75,"/"]
[null,"二氧化硫",100,55,"/"]
[null,"氮氧化物",300,206,"/"]
[null,"氯化氢",60,1.8,"/"]
[null,"一氧化碳",100,5.6,"/"]
["2018年第四季度","检测日期","2018-11-24","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"烟尘",30,1.8,2.1]
[null,"二氧化硫",100,41,22.8]
[null,"氮氧化物",300,122,181.6]
[null,"氯化氢",60,12.9,7.5]
[null,"一氧化碳",100,8.6,0.4]

{"sheet":"烟气重金属检测数据汇总","index":3,"n_rows":61,"n_cols":5,"rows_kept":61,"merged":[[0,0,0,4],[1,0,5,0],[6,0,10,0],[11,0,15,0],[16,0,20,0],[21,0,25,0],[26,0,30,0],[31,0,35,0],[36,0,40,0],[41,0,45,0],[46,0,50,0],[51,0,55,0],[56,0,60,0]]}
["延吉天楹环保能源有限公司烟气重金属检测数据汇总"]
["2018-01-01","检测日期","2018.1.20","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"汞及其化合物",0.05,"/",5.8E-5]
[null,"镉及其化合物",0.1,"/","＜0.0008"]
[null,"铅及其化合物",1,"/","＜0.002"]
["2018-02-01","检测日期","2018.2.25","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"汞及其化合物",0.05,"/",5.3e-05]
[null,"镉及其化合物",0.1,"/","＜0.0008"]
[null,"铅及其化合物",1,"/","＜0.002"]
["2018-03-01","检测日期","2018.3.19","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"汞及其化合物",0.05,"/",7e-05]
[null,"镉及其化合物",0.1,"/","＜0.0008"]
[null,"铅及其化合物",1,"/","＜0.002"]
["2018-04-01","检测日期","2018.4.24","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"汞及其化合物",0.05,6e-05,"/"]
[null,"镉及其化合物",0.1,"＜0.0008","/"]
[null,"铅及其化合物",1,"＜0.002","/"]
["2018-05-01","检测日期","2018.5.18","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"汞及其化合物",0.05,"/",5.2e-05]
[null,"镉及其化合物",0.1,"/","＜0.0008"]
[null,"铅及其化合物",1,"/","＜0.002"]
["2018-06-01","检测日期","2018.6.26","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"汞及其化合物",0.05,3.8e-05,4.4e-05]
[null,"镉及其化合物",0.1,"＜0.0008","＜0.0008"]
[null,"铅及其化合物",1,"＜0.002",0.04]
["2018-07-01","检测日期","2018.7.8","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"汞及其化合物",0.05,1e-05,5.3e-05]
[null,"镉及其化合物",0.1,"＜0.0008",0.0007]
[null,"铅及其化合物",1,"＜0.002",0.004]
["2018-08-01","检测日期","2018.8.20","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"汞及其化合物",0.05,"/",4.2e-05]
[null,"镉及其化合物",0.1,"/","＜0.0008"]
[null,"铅及其化合物",1,"/","＜0.002"]
["2018-09-01","检测日期","2018.9.28","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"汞及其化合物",0.05,"＜0.000003","/"]
[null,"镉及其化合物",0.1,"＜0.0008","/"]
[null,"铅及其化合物",1,"＜0.002","/"]
["2018-10-01","检测日期","2018.10.25","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"汞及其化合物",0.05,"＜0.000003",9.37e-06]
[null,"镉及其化合物",0.1,"＜0.0008","＜0.0008"]
[null,"铅及其化合物",1,"＜0.002","＜0.002"]
["2018-11-01","检测日期","2018.11.18","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"汞及其化合物",0.05,5.58e-05,8.52e-05]
[null,"镉及其化合物",0.1,"＜0.0008","＜0.0008"]
[null,"铅及其化合物",1,"＜0.002",0.007]
["2018-12-01","检测日期","2018.12.07","检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目","标准（mg/m3)","1#","2#"]
[null,"汞及其化合物",0.05,"＜0.000003","/"]
[null,"镉及其化合物",0.1,"＜0.0008","/"]
[null,"铅及其化合物",1,"＜0.002","/"]

{"sheet":"废水检测数据汇总","index":4,"n_rows":121,"n_cols":6,"rows_kept":121,"merged":[[0,0,0,6],[1,0,8,0],[1,2,1,3],[1,5,1,6],[2,1,2,2],[2,3,2,4],[2,5,2,6],[3,1,3,2],[3,3,3,4],[3,5,3,6],[4,1,4,2],[4,3,4,4],[4,5,4,6],[5,1,5,2],[5,3,5,4],[5,5,5,6],[6,1,6,2],[6,3,6,4],[6,5,6,6],[7,1,7,2],[7,3,7,4],[7,5,7,6],[8,1,8,2],[8,3,8,4],[8,5,8,6],[9,0,16,0],[9,2,9,3],[9,5,9,6],[10,1,10,2],[10,3,10,4],[10,5,10,6],[11,1,11,2],[11,3,11,4],[11,5,11,6],[12,1,12,2],[12,3,12,4],[12,5,12,6],[13,1,13,2],[13,3,13,4],[13,5,13,6],[14,1,14,2],[14,3,14,4],[14,5,14,6],[15,1,15,2],[15,3,15,4],[15,5,15,6],[16,1,16,2],[16,3,16,4],[16,5,16,6],[17,0,30,0],[17,2,17,3],[17,5,17,6],[18,1,18,2],[18,3,18,4],[18,5,18,6],[19,1,19,2],[19,3,19,4],[19,5,19,6],[20,1,20,2],[20,3,20,4],[20,5,20,6],[21,1,21,2],[21,3,21,4],[21,5,21,6],[22,1,22,2],[22,3,22,4],[22,5,22,6],[23,1,23,2],[23,3,23,4],[23,5,23,6],[24,1,24,2],[24,3,24,4],[24,5,24,6],[25,1,25,2],[25,3,25,4],[25,5,25,6],[26,1,26,2],[26,3,26,4],[26,5,26,6],[27,1,27,2],[27,3,27,4],[27,5,27,6],[28,1,28,2],[28,3,28,4],[28,5,28,6],[29,1,29,2],[29,3,29,4],[29,5,29,6],[30,1,30,2],[30,3,30,4],[30,5,30,6],[31,0,38,0],[31,2,31,3],[31,5,31,6],[32,1,32,2],[32,3,32,4],[32,5,32,6],[33,1,33,2],[33,3,33,4],[33,5,33,6],[34,1,34,2],[34,3,34,4],[34,5,34,6],[35,1,35,2],[35,3,35,4],[35,5,35,6],[36,1,36,2],[36,3,36,4],[36,5,36,6],[37,1,37,2],[37,3,37,4],[37,5,37,6],[38,1,38,2],[38,3,38,4],[38,5,38,6],[39,0,46,0],[39,2,39,3],[39,5,39,6],[40,1,40,2],[40,3,40,4],[40,5,40,6],[41,1,41,2],[41,3,41,4],[41,5,41,6],[42,1,42,2],[42,3,42,4],[42,5,42,6],[43,1,43,2],[43,3,43,4],[43,5,43,6],[44,1,44,2],[44,3,44,4],[44,5,44,6],[45,1,45,2],[45,3,45,4],[45,5,45,6],[46,1,46,2],[46,3,46,4],[46,5,46,6],[47,0,60,0],[47,2,47,3],[47,5,47,6],[48,1,48,2],[48,3,48,4],[48,5,48,6],[49,1,49,2],[49,3,49,4],[49,5,49,6],[50,1,50,2],[50,3,50,4],[50,5,50,6],[51,1,51,2],[51,3,51,4],[51,5,51,6],[52,1,52,2],[52,3,52,4],[52,5,52,6],[53,1,53,2],[53,3,53,4],[53,5,53,6],[54,1,54,2],[54,3,54,4],[54,5,54,6],[55,1,55,2],[55,3,55,4],[55,5,55,6],[56,1,56,2],[56,3,56,4],[56,5,56,6],[57,1,57,2],[57,3,57,4],[57,5,57,6],[58,1,58,2],[58,3,58,4],[58,5,58,6],[59,1,59,2],[59,3,59,4],[59,5,59,6],[60,1,60,2],[60,3,60,4],[60,5,60,6],[61,0,68,0],[61,2,61,3],[61,5,61,6],[62,1,62,2],[62,3,62,4],[62,5,62,6],[63,1,63,2],[63,3,63,4],[63,5,63,6],[64,1,64,2],[64,3,64,4],[64,5,64,6],[65,1,65,2],[65,3,65,4],[65,5,65,6],[66,1,66,2],[66,3,66,4],[66,5,66,6],[67,1,67,2],[67,3,67,4],[67,5,67,6],[68,1,68,2],[68,3,68,4],[68,5,68,6],[69,0,76,0],[69,2,69,3],[69,5,69,6],[70,1,70,2],[70,3,70,4],[70,5,70,6],[71,1,71,2],[71,3,71,4],[71,5,71,6],[72,1,72,2],[72,3,72,4],[72,5,72,6],[73,1,73,2],[73,3,73,4],[73,5,73,6],[74,1,74,2],[74,3,74,4],[74,5,74,6],[75,1,75,2],[75,3,75,4],[75,5,75,6],[76,1,76,2],[76,3,76,4],[76,5,76,6],[77,0,90,0],[77,2,77,3],[77,5,77,6],[78,1,78,2],[78,3,78,4],[78,5,78,6],[79,1,79,2],[79,3,79,4],[79,5,79,6],[80,1,80,2],[80,3,80,4],[80,5,80,6],[81,1,81,2],[81,3,81,4],[81,5,81,6],[82,1,82,2],[82,3,82,4],[82,5,82,6],[83,1,83,2],[83,3,83,4],[83,5,83,6],[84,1,84,2],[84,3,84,4],[84,5,84,6],[85,1,85,2],[85,3,85,4],[85,5,85,6],[86,1,86,2],[86,3,86,4],[86,5,86,6],[87,1,87,2],[87,3,87,4],[87,5,87,6],[88,1,88,2],[88,3,88,4],[88,5,88,6],[89,1,89,2],[89,3,89,4],[89,5,89,6],[90,1,90,2],[90,3,90,4],[90,5,90,6],[91,0,98,0],[91,2,91,3],[91,5,91,6],[92,1,92,2],[92,3,92,4],[92,5,92,6],[93,1,93,2],[93,3,93,4],[93,5,93,6],[94,1,94,2],[94,3,94,4],[94,5,94,6],[95,1,95,2],[95,3,95,4],[95,5,95,6],[96,1,96,2],[96,3,96,4],[96,5,96,6],[97,1,97,2],[97,3,97,4],[97,5,97,6],[98,1,98,2],[98,3,98,4],[98,5,98,6],[99,0,112,0],[99,2,99,3],[99,5,99,6],[100,1,100,2],[100,3,100,4],[100,5,100,6],[101,1,101,2],[101,3,101,4],[101,5,101,6],[102,1,102,2],[102,3,102,4],[102,5,102,6],[103,1,103,2],[103,3,103,4],[103,5,103,6],[104,1,104,2],[104,3,104,4],[104,5,104,6],[105,1,105,2],[105,3,105,4],[105,5,105,6],[106,1,106,2],[106,3,106,4],[106,5,106,6],[107,1,107,2],[107,3,107,4],[107,5,107,6],[108,1,108,2],[108,3,108,4],[108,5,108,6],[109,1,109,2],[109,3,109,4],[109,5,109,6],[110,1,110,2],[110,3,110,4],[110,5,110,6],[111,1,111,2],[111,3,111,4],[111,5,111,6],[112,1,112,2],[112,3,112,4],[112,5,112,6],[113,0,120,0],[113,2,113,3],[113,5,113,6],[114,1,114,2],[114,3,114,4],[114,5,114,6],[115,1,115,2],[115,3,115,4],[115,5,115,6],[116,1,116,2],[116,3,116,4],[116,5,116,6],[117,1,117,2],[117,3,117,4],[117,5,117,6],[118,1,118,2],[118,3,118,4],[118,5,118,6],[119,1,119,2],[119,3,119,4],[119,5,119,6],[120,1,120,2],[120,3,120,4],[120,5,120,6]]}
["延吉天楹环保能源有限公司废水检测数据汇总"]
["2018-01-11","检测日期","2018-01-20",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"《生活垃圾填埋场污染控制标准》（GB16889-2008)",null,"检测结果（除注明外，单位mg/L）"]
[null,"六价铬",null,0.05,null,0.044]
[null,"总砷",null,0.1,null,0.0006]
[null,"总汞",null,1E-3,null,0.00016]
[null,"总铅",null,0.1,null,"未检出"]
[null,"总镉",null,0.01,null,"未检出"]
[null,"总铬",null,0.1,null,0.079]
["2018-02-11","检测日期","2018-02-25",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"《生活垃圾填埋场污染控制标准》（GB16889-2008)",null,"检测结果（除注明外，单位mg/L）"]
[null,"六价铬",null,0.05,null,0.012]
[null,"总砷",null,0.1,null,0.0007]
[null,"总汞",null,1E-3,null,1.2E-4]
[null,"总铅",null,0.1,null,"未检出"]
[null,"总镉",null,0.01,null,0.004]
[null,"总铬",null,0.1,null,0.02]
["2018-03-11","检测日期","2018-03-19",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"《污水综合排放标准》（GB8978-1996)《生活垃圾填埋场污染控制标准》（GB16889-2008)",null,"检测结果（除注明外，单位mg/L）"]
[null,"pH值",null,"6--9",null,6.65]
[null,"悬浮物",null,400,null,5]
[null,"化学需氧量",null,500,null,28]
[null,"氨氮",null,25,null,1.55]
[null,"总磷",null,5,null,0.96]
[null,"石油类",null,30,null,0.45]
[null,"总镉",null,0.01,null,0.005]
[null,"总汞",null,1E-3,null,0.00014]
[null,"总砷",null,0.1,null,0.0036]
[null,"总铬",null,0.1,null,0.006]
[null,"总铅",null,0.1,null,0.046]
[null,"六价铬",null,0.05,null,"未检出"]
["2018-04-11","检测日期","2018-04-24",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"《生活垃圾填埋场污染控制标准》（GB16889-2008)",null,"检测结果（除注明外，单位mg/L）"]
[null,"六价铬",null,0.05,null,0.045]
[null,"总砷",null,0.1,null,0.0045]
[null,"总汞",null,1E-3,null,0.00016]
[null,"总铅",null,0.1,null,"未检出"]
[null,"总镉",null,0.01,null,"未检出"]
[null,"总铬",null,0.1,null,0.07]
["2018-05-11","检测日期","2018-05-18",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"《生活垃圾填埋场污染控制标准》（GB16889-2008)",null,"检测结果（除注明外，单位mg/L）"]
[null,"六价铬",null,0.05,null,0.006]
[null,"总砷",null,0.1,null,0.0031]
[null,"总汞",null,1E-3,null,"未检出"]
[null,"总铅",null,0.1,null,"未检出"]
[null,"总镉",null,0.01,null,1E-3]
[null,"总铬",null,0.1,null,0.01]
["2018-06-11","检测日期","2018-06-26",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"《污水综合排放标准》（GB8978-1996)《生活垃圾填埋场污染控制标准》（GB16889-2008)",null,"检测结果（除注明外，单位mg/L）"]
[null,"pH值",null,"6--9",null,7.74]
[null,"悬浮物",null,400,null,89]
[null,"化学需氧量",null,500,null,57]
[null,"氨氮",null,25,null,8.32]
[null,"总磷",null,5,null,2.51]
[null,"石油类",null,30,null,0.14]
[null,"总镉",null,0.01,null,"未检出"]
[null,"总汞",null,1E-3,null,0.00055]
[null,"总砷",null,0.1,null,0.0045]
[null,"总铬",null,0.1,null,0.011]
[null,"总铅",null,0.1,null,"未检出"]
[null,"六价铬",null,0.05,null,0.008]
["2018-07-11","检测日期","2018-07-08",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"《生活垃圾填埋场污染控制标准》（GB16889-2008)",null,"检测结果（除注明外，单位mg/L）"]
[null,"六价铬",null,0.05,null,"未检出"]
[null,"总砷",null,0.1,null,0.0029]
[null,"总汞",null,1E-3,null,0.00047]
[null,"总铅",null,0.1,null,"未检出"]
[null,"总镉",null,0.01,null,"未检出"]
[null,"总铬",null,0.1,null,"未检出"]
["2018-08-11","检测日期","2018-08-20",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"《生活垃圾填埋场污染控制标准》（GB16889-2008)",null,"检测结果（除注明外，单位mg/L）"]
[null,"六价铬",null,0.05,null,"未检出"]
[null,"总砷",null,0.1,null,2.3E-3]
[null,"总汞",null,1E-3,null,0.00032]
[null,"总铅",null,0.1,null,"未检出"]
[null,"总镉",null,0.01,null,"未检出"]
[null,"总铬",null,0.1,null,"未检出"]
["2018-09-11","检测日期","2018-09-28",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"《污水综合排放标准》（GB8978-1996)《生活垃圾填埋场污染控制标准》（GB16889-2008)",null,"检测结果（除注明外，单位mg/L）"]
[null,"pH值",null,"6--9",null,6.97]
[null,"悬浮物",null,400,null,6]
[null,"化学需氧量",null,500,null,72]
[null,"氨氮",null,25,null,3.24]
[null,"总磷",null,5,null,1.78]
[null,"石油类",null,30,null,0.21]
[null,"总镉",null,0.01,null,"未检出"]
[null,"总汞",null,1E-3,null,3.1E-4]
[null,"总砷",null,0.1,null,0.0044]
[null,"总铬",null,0.1,null,0.06]
[null,"总铅",null,0.1,null,"未检出"]
[null,"六价铬",null,0.05,null,0.01]
["2018-10-11","检测日期","2018-10-25",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"《生活垃圾填埋场污染控制标准》（GB16889-2008)",null,"检测结果（除注明外，单位mg/L）"]
[null,"六价铬",null,0.05,null,"未检出"]
[null,"总砷",null,0.1,null,0.0027]
[null,"总汞",null,1E-3,null,0.00025]
[null,"总铅",null,0.1,null,"未检出"]
[null,"总镉",null,0.01,null,"未检出"]
[null,"总铬",null,0.1,null,"未检出"]
["2018-11-11","检测日期","2018-11-24",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"《污水综合排放标准》（GB8978-1996)《生活垃圾填埋场污染控制标准》（GB16889-2008)",null,"检测结果（除注明外，单位mg/L）"]
[null,"pH值",null,"6--9",null,8.38]
[null,"悬浮物",null,400,null,31]
[null,"化学需氧量",null,500,null,45]
[null,"氨氮",null,25,null,4.12]
[null,"总磷",null,5,null,1.92]
[null,"石油类",null,30,null,0.17]
[null,"总镉",null,0.01,null,"未检出"]
[null,"总汞",null,1E-3,null,0.00019]
[null,"总砷",null,0.1,null,4.3E-3]
[null,"总铬",null,0.1,null,0.012]
[null,"总铅",null,0.1,null,"未检出"]
[null,"六价铬",null,0.05,null,"未检出"]
["2018-12-11","检测日期","2018-12-07",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"《生活垃圾填埋场污染控制标准》（GB16889-2008)",null,"检测结果（除注明外，单位mg/L）"]
[null,"六价铬",null,0.05,null,"未检出"]
[null,"总砷",null,0.1,null,0.0026]
[null,"总汞",null,1E-3,null,7e-05]
[null,"总铅",null,0.1,null,"未检出"]
[null,"总镉",null,0.01,null,"未检出"]
[null,"总铬",null,0.1,null,0.015]

{"sheet":"飞灰检测数据汇总","index":5,"n_rows":193,"n_cols":7,"rows_kept":193,"merged":[[0,1,0,7],[1,1,16,1],[1,3,1,4],[1,6,1,7],[2,2,2,3],[2,4,2,5],[2,6,2,7],[3,2,3,3],[3,4,3,5],[3,6,3,7],[4,2,4,3],[4,4,4,5],[4,6,4,7],[5,2,5,3],[5,4,5,5],[5,6,5,7],[6,2,6,3],[6,4,6,5],[6,6,6,7],[7,2,7,3],[7,4,7,5],[7,6,7,7],[8,2,8,3],[8,4,8,5],[8,6,8,7],[9,2,9,3],[9,4,9,5],[9,6,9,7],[10,2,10,3],[10,4,10,5],[10,6,10,7],[11,2,11,3],[11,4,11,5],[11,6,11,7],[12,2,12,3],[12,4,12,5],[12,6,12,7],[13,2,13,3],[13,4,13,5],[13,6,13,7],[14,2,14,3],[14,4,14,5],[14,6,14,7],[15,2,15,3],[15,4,15,5],[15,6,15,7],[16,2,16,3],[16,4,16,5],[16,6,16,7],[17,1,32,1],[17,3,17,4],[17,6,17,7],[18,2,18,3],[18,4,18,5],[18,6,18,7],[19,2,19,3],[19,4,19,5],[19,6,19,7],[20,2,20,3],[20,4,20,5],[20,6,20,7],[21,2,21,3],[21,4,21,5],[21,6,21,7],[22,2,22,3],[22,4,22,5],[22,6,22,7],[23,2,23,3],[23,4,23,5],[23,6,23,7],[24,2,24,3],[24,4,24,5],[24,6,24,7],[25,2,25,3],[25,4,25,5],[25,6,25,7],[26,2,26,3],[26,4,26,5],[26,6,26,7],[27,2,27,3],[27,4,27,5],[27,6,27,7],[28,2,28,3],[28,4,28,5],[28,6,28,7],[29,2,29,3],[29,4,29,5],[29,6,29,7],[30,2,30,3],[30,4,30,5],[30,6,30,7],[31,2,31,3],[31,4,31,5],[31,6,31,7],[32,2,32,3],[32,4,32,5],[32,6,32,7],[33,1,48,1],[33,3,33,4],[33,6,33,7],[34,2,34,3],[34,4,34,5],[34,6,34,7],[35,2,35,3],[35,4,35,5],[35,6,35,7],[36,2,36,3],[36,4,36,5],[36,6,36,7],[37,2,37,3],[37,4,37,5],[37,6,37,7],[38,2,38,3],[38,4,38,5],[38,6,38,7],[39,2,39,3],[39,4,39,5],[39,6,39,7],[40,2,40,3],[40,4,40,5],[40,6,40,7],[41,2,41,3],[41,4,41,5],[41,6,41,7],[42,2,42,3],[42,4,42,5],[42,6,42,7],[43,2,43,3],[43,4,43,5],[43,6,43,7],[44,2,44,3],[44,4,44,5],[44,6,44,7],[45,2,45,3],[45,4,45,5],[45,6,45,7],[46,2,46,3],[46,4,46,5],[46,6,46,7],[47,2,47,3],[47,4,47,5],[47,6,47,7],[48,2,48,3],[48,4,48,5],[48,6,48,7],[49,1,64,1],[49,3,49,4],[49,6,49,7],[50,2,50,3],[50,4,50,5],[50,6,50,7],[51,2,51,3],[51,4,51,5],[51,6,51,7],[52,2,52,3],[52,4,52,5],[52,6,52,7],[53,2,53,3],[53,4,53,5],[53,6,53,7],[54,2,54,3],[54,4,54,5],[54,6,54,7],[55,2,55,3],[55,4,55,5],[55,6,55,7],[56,2,56,3],[56,4,56,5],[56,6,56,7],[57,2,57,3],[57,4,57,5],[57,6,57,7],[58,2,58,3],[58,4,58,5],[58,6,58,7],[59,2,59,3],[59,4,59,5],[59,6,59,7],[60,2,60,3],[60,4,60,5],[60,6,60,7],[61,2,61,3],[61,4,61,5],[61,6,61,7],[62,2,62,3],[62,4,62,5],[62,6,62,7],[63,2,63,3],[63,4,63,5],[63,6,63,7],[64,2,64,3],[64,4,64,5],[64,6,64,7],[65,1,80,1],[65,3,65,4],[65,6,65,7],[66,2,66,3],[66,4,66,5],[66,6,66,7],[67,2,67,3],[67,4,67,5],[67,6,67,7],[68,2,68,3],[68,4,68,5],[68,6,68,7],[69,2,69,3],[69,4,69,5],[69,6,69,7],[70,2,70,3],[70,4,70,5],[70,6,70,7],[71,2,71,3],[71,4,71,5],[71,6,71,7],[72,2,72,3],[72,4,72,5],[72,6,72,7],[73,2,73,3],[73,4,73,5],[73,6,73,7],[74,2,74,3],[74,4,74,5],[74,6,74,7],[75,2,75,3],[75,4,75,5],[75,6,75,7],[76,2,76,3],[76,4,76,5],[76,6,76,7],[77,2,77,3],[77,4,77,5],[77,6,77,7],[78,2,78,3],[78,4,78,5],[78,6,78,7],[79,2,79,3],[79,4,79,5],[79,6,79,7],[80,2,80,3],[80,4,80,5],[80,6,80,7],[81,1,96,1],[81,3,81,4],[81,6,81,7],[82,2,82,3],[82,4,82,5],[82,6,82,7],[83,2,83,3],[83,4,83,5],[83,6,83,7],[84,2,84,3],[84,4,84,5],[84,6,84,7],[85,2,85,3],[85,4,85,5],[85,6,85,7],[86,2,86,3],[86,4,86,5],[86,6,86,7],[87,2,87,3],[87,4,87,5],[87,6,87,7],[88,2,88,3],[88,4,88,5],[88,6,88,7],[89,2,89,3],[89,4,89,5],[89,6,89,7],[90,2,90,3],[90,4,90,5],[90,6,90,7],[91,2,91,3],[91,4,91,5],[91,6,91,7],[92,2,92,3],[92,4,92,5],[92,6,92,7],[93,2,93,3],[93,4,93,5],[93,6,93,7],[94,2,94,3],[94,4,94,5],[94,6,94,7],[95,2,95,3],[95,4,95,5],[95,6,95,7],[96,2,96,3],[96,4,96,5],[96,6,96,7],[97,1,112,1],[97,3,97,4],[97,6,97,7],[98,2,98,3],[98,4,98,5],[98,6,98,7],[99,2,99,3],[99,4,99,5],[99,6,99,7],[100,2,100,3],[100,4,100,5],[100,6,100,7],[101,2,101,3],[101,4,101,5],[101,6,101,7],[102,2,102,3],[102,4,102,5],[102,6,102,7],[103,2,103,3],[103,4,103,5],[103,6,103,7],[104,2,104,3],[104,4,104,5],[104,6,104,7],[105,2,105,3],[105,4,105,5],[105,6,105,7],[106,2,106,3],[106,4,106,5],[106,6,106,7],[107,2,107,3],[107,4,107,5],[107,6,107,7],[108,2,108,3],[108,4,108,5],[108,6,108,7],[109,2,109,3],[109,4,109,5],[109,6,109,7],[110,2,110,3],[110,4,110,5],[110,6,110,7],[111,2,111,3],[111,4,111,5],[111,6,111,7],[112,2,112,3],[112,4,112,5],[112,6,112,7],[113,1,128,1],[113,3,113,4],[113,6,113,7],[114,2,114,3],[114,4,114,5],[114,6,114,7],[115,2,115,3],[115,4,115,5],[115,6,115,7],[116,2,116,3],[116,4,116,5],[116,6,116,7],[117,2,117,3],[117,4,117,5],[117,6,117,7],[118,2,118,3],[118,4,118,5],[118,6,118,7],[119,2,119,3],[119,4,119,5],[119,6,119,7],[120,2,120,3],[120,4,120,5],[120,6,120,7],[121,2,121,3],[121,4,121,5],[121,6,121,7],[122,2,122,3],[122,4,122,5],[122,6,122,7],[123,2,123,3],[123,4,123,5],[123,6,123,7],[124,2,124,3],[124,4,124,5],[124,6,124,7],[125,2,125,3],[125,4,125,5],[125,6,125,7],[126,2,126,3],[126,4,126,5],[126,6,126,7],[127,2,127,3],[127,4,127,5],[127,6,127,7],[128,2,128,3],[128,4,128,5],[128,6,128,7],[129,1,144,1],[129,3,129,4],[129,6,129,7],[130,2,130,3],[130,4,130,5],[130,6,130,7],[131,2,131,3],[131,4,131,5],[131,6,131,7],[132,2,132,3],[132,4,132,5],[132,6,132,7],[133,2,133,3],[133,4,133,5],[133,6,133,7],[134,2,134,3],[134,4,134,5],[134,6,134,7],[135,2,135,3],[135,4,135,5],[135,6,135,7],[136,2,136,3],[136,4,136,5],[136,6,136,7],[137,2,137,3],[137,4,137,5],[137,6,137,7],[138,2,138,3],[138,4,138,5],[138,6,138,7],[139,2,139,3],[139,4,139,5],[139,6,139,7],[140,2,140,3],[140,4,140,5],[140,6,140,7],[141,2,141,3],[141,4,141,5],[141,6,141,7],[142,2,142,3],[142,4,142,5],[142,6,142,7],[143,2,143,3],[143,4,143,5],[143,6,143,7],[144,2,144,3],[144,4,144,5],[144,6,144,7],[145,1,160,1],[145,3,145,4],[145,6,145,7],[146,2,146,3],[146,4,146,5],[146,6,146,7],[147,2,147,3],[147,4,147,5],[147,6,147,7],[148,2,148,3],[148,4,148,5],[148,6,148,7],[149,2,149,3],[149,4,149,5],[149,6,149,7],[150,2,150,3],[150,4,150,5],[150,6,150,7],[151,2,151,3],[151,4,151,5],[151,6,151,7],[152,2,152,3],[152,4,152,5],[152,6,152,7],[153,2,153,3],[153,4,153,5],[153,6,153,7],[154,2,154,3],[154,4,154,5],[154,6,154,7],[155,2,155,3],[155,4,155,5],[155,6,155,7],[156,2,156,3],[156,4,156,5],[156,6,156,7],[157,2,157,3],[157,4,157,5],[157,6,157,7],[158,2,158,3],[158,4,158,5],[158,6,158,7],[159,2,159,3],[159,4,159,5],[159,6,159,7],[160,2,160,3],[160,4,160,5],[160,6,160,7],[161,1,176,1],[161,3,161,4],[161,6,161,7],[162,2,162,3],[162,4,162,5],[162,6,162,7],[163,2,163,3],[163,4,163,5],[163,6,163,7],[164,2,164,3],[164,4,164,5],[164,6,164,7],[165,2,165,3],[165,4,165,5],[165,6,165,7],[166,2,166,3],[166,4,166,5],[166,6,166,7],[167,2,167,3],[167,4,167,5],[167,6,167,7],[168,2,168,3],[168,4,168,5],[168,6,168,7],[169,2,169,3],[169,4,169,5],[169,6,169,7],[170,2,170,3],[170,4,170,5],[170,6,170,7],[171,2,171,3],[171,4,171,5],[171,6,171,7],[172,2,172,3],[172,4,172,5],[172,6,172,7],[173,2,173,3],[173,4,173,5],[173,6,173,7],[174,2,174,3],[174,4,174,5],[174,6,174,7],[175,2,175,3],[175,4,175,5],[175,6,175,7],[176,2,176,3],[176,4,176,5],[176,6,176,7],[177,1,192,1],[177,3,177,4],[177,6,177,7],[178,2,178,3],[178,4,178,5],[178,6,178,7],[179,2,179,3],[179,4,179,5],[179,6,179,7],[180,2,180,3],[180,4,180,5],[180,6,180,7],[181,2,181,3],[181,4,181,5],[181,6,181,7],[182,2,182,3],[182,4,182,5],[182,6,182,7],[183,2,183,3],[183,4,183,5],[183,6,183,7],[184,2,184,3],[184,4,184,5],[184,6,184,7],[185,2,185,3],[185,4,185,5],[185,6,185,7],[186,2,186,3],[186,4,186,5],[186,6,186,7],[187,2,187,3],[187,4,187,5],[187,6,187,7],[188,2,188,3],[188,4,188,5],[188,6,188,7],[189,2,189,3],[189,4,189,5],[189,6,189,7],[190,2,190,3],[190,4,190,5],[190,6,190,7],[191,2,191,3],[191,4,191,5],[191,6,191,7],[192,2,192,3],[192,4,192,5],[192,6,192,7]]}
[null,"延吉天楹环保能源有限公司飞灰检测数据汇总"]
[null,"2018-01-20","检测日期","2018-01-20",null,"检测单位","大连华信理化检测中心有限公司"]
[null,null,"检测项目",null,"标准（除注明外，单位mg/L）",null,"检测结果（除注明外，单位mg/L）"]
[null,null,"含水率（%）",null,30,null,18.3]
[null,null,"钡",null,25,null,1.3]
[null,null,"铍",null,0.02,null,"未检出"]
[null,null,"镉",null,0.15,null,0.0226]
[null,null,"总铬",null,4.5,null,0.248]
[null,null,"铜",null,40,null,0.16]
[null,null,"镍",null,0.5,null,0.46]
[null,null,"铅",null,0.25,null,0.176]
[null,null,"硒",null,0.1,null,3.3E-3]
[null,null,"锌",null,100,null,5.51]
[null,null,"汞",null,0.05,null,"未检出"]
[null,null,"砷",null,0.3,null,0.00778]
[null,null,"六价铬",null,1.5,null,0.013]
[null,null,"二噁英",null,"3（μg/kg）",null,0.38]
[null,"2018-02-25","检测日期","2018-02-25",null,"检测单位","大连华信理化检测中心有限公司"]
[null,null,"检测项目",null,"标准（除注明外，单位mg/L）",null,"检测结果（除注明外，单位mg/L）"]
[null,null,"含水率（%）",null,30,null,20.34]
[null,null,"汞",null,0.05,null,0.0006]
[null,null,"铜",null,40,null,0.18]
[null,null,"锌",null,100,null,11.8]
[null,null,"铅",null,0.25,null,0.074]
[null,null,"镉",null,0.15,null,0.0222]
[null,null,"铍",null,0.02,null,"未检出"]
[null,null,"钡",null,25,null,1.66]
[null,null,"镍",null,0.5,null,0.44]
[null,null,"砷",null,0.3,null,0.0294]
[null,null,"总铬",null,4.5,null,0.01]
[null,null,"六价铬",null,1.5,null,0.008]
[null,null,"硒",null,0.1,null,0.00872]
[null,null,"二噁英",null,"3（μg/kg）",null,0.084]
[null,"2018-03-19","检测日期","2018-03-19",null,"检测单位","大连华信理化检测中心有限公司"]
[null,null,"检测项目",null,"标准（除注明外，单位mg/L）",null,"检测结果（除注明外，单位mg/L）"]
[null,null,"含水率（%）",null,30,null,20.22]
[null,null,"汞",null,0.05,null,"未检出"]
[null,null,"铜",null,40,null,0.14]
[null,null,"锌",null,100,null,0.187]
[null,null,"铅",null,0.25,null,0.053]
[null,null,"镉",null,0.15,null,0.023]
[null,null,"铍",null,0.02,null,"未检出"]
[null,null,"钡",null,25,null,1.45]
[null,null,"镍",null,0.5,null,0.26]
[null,null,"砷",null,0.3,null,0.018]
[null,null,"总铬",null,4.5,null,0.051]
[null,null,"六价铬",null,1.5,null,0.014]
[null,null,"硒",null,0.1,null,0.0243]
[null,null,"二噁英",null,"3（μg/kg）",null,0.22]
[null,"2018-04-20","检测日期","2018-04-24",null,"检测单位","大连华信理化检测中心有限公司"]
[null,null,"检测项目",null,"标准（除注明外，单位mg/L）",null,"检测结果（除注明外，单位mg/L）"]
[null,null,"含水率（%）",null,30,null,20.8]
[null,null,"钡",null,25,null,1.63]
[null,null,"铍",null,0.02,null,"未检出"]
[null,null,"镉",null,0.15,null,"未检出"]
[null,null,"总铬",null,4.5,null,0.012]
[null,null,"铜",null,40,null,0.18]
[null,null,"镍",null,0.5,null,0.47]
[null,null,"铅",null,0.25,null,0.25]
[null,null,"硒",null,0.1,null,0.00137]
[null,null,"锌",null,100,null,8.8]
[null,null,"汞",null,0.05,null,"未检出"]
[null,null,"砷",null,0.3,null,0.0139]
[null,null,"六价铬",null,1.5,null,0.01]
[null,null,"二噁英",null,"3（μg/kg）",null,0.22]
[null,"2018-05-25","检测日期","2018-05-18",null,"检测单位","大连华信理化检测中心有限公司"]
[null,null,"检测项目",null,"标准（除注明外，单位mg/L）",null,"检测结果（除注明外，单位mg/L）"]
[null,null,"含水率（%）",null,30,null,22.89]
[null,null,"汞",null,0.05,null,1.5E-3]
[null,null,"铜",null,40,null,0.16]
[null,null,"锌",null,100,null,0.094]
[null,null,"铅",null,0.25,null,0.028]
[null,null,"镉",null,0.15,null,2E-3]
[null,null,"铍",null,0.02,null,"未检出"]
[null,null,"钡",null,25,null,1.01]
[null,null,"镍",null,0.5,null,0.46]
[null,null,"砷",null,0.3,null,0.00532]
[null,null,"总铬",null,4.5,null,0.124]
[null,null,"六价铬",null,1.5,null,0.009]
[null,null,"硒",null,0.1,null,0.00358]
[null,null,"二噁英",null,"3（μg/kg）",null,0.21]
[null,"2018-06-19","检测日期","2018-06-29",null,"检测单位","大连华信理化检测中心有限公司"]
[null,null,"检测项目",null,"标准（除注明外，单位mg/L）",null,"检测结果（除注明外，单位mg/L）"]
[null,null,"含水率（%）",null,30,null,24.5]
[null,null,"汞",null,0.05,null,"未检出"]
[null,null,"铜",null,40,null,0.17]
[null,null,"锌",null,100,null,0.274]
[null,null,"铅",null,0.25,null,0.058]
[null,null,"镉",null,0.15,null,0.003]
[null,null,"铍",null,0.02,null,"未检出"]
[null,null,"钡",null,25,null,1.22]
[null,null,"镍",null,0.5,null,0.39]
[null,null,"砷",null,0.3,null,0.0039]
[null,null,"总铬",null,4.5,null,0.052]
[null,null,"六价铬",null,1.5,null,0.008]
[null,null,"硒",null,0.1,null,0.00204]
[null,null,"二噁英",null,"3（μg/kg）",null,0.054]
[null,"2018-07-20","检测日期","2018-07-08",null,"检测单位","大连华信理化检测中心有限公司"]
[null,null,"检测项目",null,"标准（除注明外，单位mg/L）",null,"检测结果（除注明外，单位mg/L）"]
[null,null,"含水率（%）",null,30,null,23.9]
[null,null,"钡",null,25,null,0.999]
[null,null,"铍",null,0.02,null,"未检出"]
[null,null,"镉",null,0.15,null,1.9E-3]
[null,null,"总铬",null,4.5,null,0.057]
[null,null,"铜",null,40,null,0.11]
[null,null,"镍",null,0.5,null,0.49]
[null,null,"铅",null,0.25,null,0.026]
[null,null,"硒",null,0.1,null,0.0098]
[null,null,"锌",null,100,null,0.192]
[null,null,"汞",null,0.05,null,0.00044]
[null,null,"砷",null,0.3,null,0.0826]
[null,null,"六价铬",null,1.5,null,"未检出"]
[null,null,"二噁英",null,"3（μg/kg）",null,0.18]
[null,"2018-08-25","检测日期","2018-08-25",null,"检测单位","大连华信理化检测中心有限公司"]
[null,null,"检测项目",null,"标准（除注明外，单位mg/L）",null,"检测结果（除注明外，单位mg/L）"]
[null,null,"含水率（%）",null,30,null,22.1]
[null,null,"汞",null,0.05,null,1.31E-3]
[null,null,"铜",null,40,null,0.12]
[null,null,"锌",null,100,null,0.15]
[null,null,"铅",null,0.25,null,0.04]
[null,null,"镉",null,0.15,null,0.0011]
[null,null,"铍",null,0.02,null,0.0013]
[null,null,"钡",null,25,null,1.51]
[null,null,"镍",null,0.5,null,0.48]
[null,null,"砷",null,0.3,null,6.6E-4]
[null,null,"总铬",null,4.5,null,0.074]
[null,null,"六价铬",null,1.5,null,0.011]
[null,null,"硒",null,0.1,null,0.00204]
[null,null,"二噁英",null,"3（μg/kg）",null,0.089]
[null,"2018-09-19","检测日期","2018-09-28",null,"检测单位","大连华信理化检测中心有限公司"]
[null,null,"检测项目",null,"标准（除注明外，单位mg/L）",null,"检测结果（除注明外，单位mg/L）"]
[null,null,"含水率（%）",null,30,null,23.8]
[null,null,"汞",null,0.05,null,5e-05]
[null,null,"铜",null,40,null,0.19]
[null,null,"锌",null,100,null,0.213]
[null,null,"铅",null,0.25,null,0.01]
[null,null,"镉",null,0.15,null,1.4E-3]
[null,null,"铍",null,0.02,null,"未检出"]
[null,null,"钡",null,25,null,1.52]
[null,null,"镍",null,0.5,null,0.48]
[null,null,"砷",null,0.3,null,4.81E-3]
[null,null,"总铬",null,4.5,null,0.127]
[null,null,"六价铬",null,1.5,null,0.01]
[null,null,"硒",null,0.1,null,0.00078]
[null,null,"二噁英",null,"3（μg/kg）",null,0.12]
[null,"2018-10-11","检测日期","2018-10-11",null,"检测单位","大连华信理化检测中心有限公司"]
[null,null,"检测项目",null,"标准（除注明外，单位mg/L）",null,"检测结果（除注明外，单位mg/L）"]
[null,null,"含水率（%）",null,30,null,25.16]
[null,null,"汞",null,0.05,null,"未检出"]
[null,null,"铜",null,40,null,"未检出"]
[null,null,"锌",null,100,null,0.045]
[null,null,"铅",null,0.25,null,"未检出"]
[null,null,"镉",null,0.15,null,"未检出"]
[null,null,"铍",null,0.02,null,"未检出"]
[null,null,"钡",null,25,null,1.1]
[null,null,"镍",null,0.5,null,"未检出"]
[null,null,"砷",null,0.3,null,0.0016]
[null,null,"总铬",null,4.5,null,0.02]
[null,null,"六价铬",null,1.5,null,"未检出"]
[null,null,"硒",null,0.1,null,"未检出"]
[null,null,"二噁英",null,"3（μg/kg）",null,0.11]
[null,"2018-11-13","检测日期","2018-11-13",null,"检测单位","大连华信理化检测中心有限公司"]
[null,null,"检测项目",null,"标准（除注明外，单位mg/L）",null,"检测结果（除注明外，单位mg/L）"]
[null,null,"含水率（%）",null,30,null,18.08]
[null,null,"汞",null,0.05,null,0.0002]
[null,null,"铜",null,40,null,"未检出"]
[null,null,"锌",null,100,null,0.132]
[null,null,"铅",null,0.25,null,0.1]
[null,null,"镉",null,0.15,null,"未检出"]
[null,null,"铍",null,0.02,null,"未检出"]
[null,null,"钡",null,25,null,2.08]
[null,null,"镍",null,0.5,null,"未检出"]
[null,null,"砷",null,0.3,null,0.0006]
[null,null,"总铬",null,4.5,null,0.02]
[null,null,"六价铬",null,1.5,null,"未检出"]
[null,null,"硒",null,0.1,null,"未检出"]
[null,null,"二噁英",null,"3（μg/kg）",null,0.093]
[null,"2018-12-19","检测日期","2018-12-11",null,"检测单位","大连华信理化检测中心有限公司"]
[null,null,"检测项目",null,"标准（除注明外，单位mg/L）",null,"检测结果（除注明外，单位mg/L）"]
[null,null,"含水率（%）",null,30,null,18.7]
[null,null,"汞",null,0.05,null,"未检出"]
[null,null,"铜",null,40,null,"未检出"]
[null,null,"锌",null,100,null,0.15]
[null,null,"铅",null,0.25,null,0.06]
[null,null,"镉",null,0.15,null,"未检出"]
[null,null,"铍",null,0.02,null,"未检出"]
[null,null,"钡",null,25,null,1.7]
[null,null,"镍",null,0.5,null,"未检出"]
[null,null,"砷",null,0.3,null,1.5E-3]
[null,null,"总铬",null,4.5,null,0.02]
[null,null,"六价铬",null,1.5,null,"未检出"]
[null,null,"硒",null,0.1,null,"未检出"]
[null,null,"二噁英",null,"3（μg/kg）",null,0.079]

{"sheet":"炉渣热酌减率数据汇总","index":6,"n_rows":49,"n_cols":7,"rows_kept":49,"merged":[[0,0,0,6],[1,0,4,0],[1,2,1,3],[1,5,1,6],[2,1,3,2],[2,3,3,4],[2,5,2,6],[4,1,4,2],[4,3,4,4],[5,0,8,0],[5,2,5,3],[5,5,5,6],[6,1,7,2],[6,3,7,4],[6,5,6,6],[8,1,8,2],[8,3,8,4],[9,0,12,0],[9,2,9,3],[9,5,9,6],[10,1,11,2],[10,3,11,4],[10,5,10,6],[12,1,12,2],[12,3,12,4],[13,0,16,0],[13,2,13,3],[13,5,13,6],[14,1,15,2],[14,3,15,4],[14,5,14,6],[16,1,16,2],[16,3,16,4],[17,0,20,0],[17,2,17,3],[17,5,17,6],[18,1,19,2],[18,3,19,4],[18,5,18,6],[20,1,20,2],[20,3,20,4],[21,0,24,0],[21,2,21,3],[21,5,21,6],[22,1,23,2],[22,3,23,4],[22,5,22,6],[24,1,24,2],[24,3,24,4],[25,0,28,0],[25,2,25,3],[25,5,25,6],[26,1,27,2],[26,3,27,4],[26,5,26,6],[28,1,28,2],[28,3,28,4],[29,0,32,0],[29,2,29,3],[29,5,29,6],[30,1,31,2],[30,3,31,4],[30,5,30,6],[32,1,32,2],[32,3,32,4],[33,0,36,0],[33,2,33,3],[33,5,33,6],[34,1,35,2],[34,3,35,4],[34,5,34,6],[36,1,36,2],[36,3,36,4],[37,0,40,0],[37,2,37,3],[37,5,37,6],[38,1,39,2],[38,3,39,4],[38,5,38,6],[40,1,40,2],[40,3,40,4],[41,0,44,0],[41,2,41,3],[41,5,41,6],[42,1,43,2],[42,3,43,4],[42,5,42,6],[44,1,44,2],[44,3,44,4],[45,0,48,0],[45,2,45,3],[45,5,45,6],[46,1,47,2],[46,3,47,4],[46,5,46,6],[48,1,48,2],[48,3,48,4]]}
["滨州天楹环保能源有限公司炉渣热酌减率检测数据汇总"]
["2018-01-01","检测日期","2018-01-20",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"标准（%）",null,"检测结果（%）"]
[{"$nulls":5},"1#","2#"]
[null,"热酌减率",null,5,null,"停炉",2.2]
["2018-02-01","检测日期","2018-02-25",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"标准（%）",null,"检测结果（%）"]
[{"$nulls":5},"1#","2#"]
[null,"热酌减率",null,5,null,"停炉",2.65]
["2018-03-01","检测日期","2018-03-19",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"标准（%）",null,"检测结果（%）"]
[{"$nulls":5},"1#","2#"]
[null,"热酌减率",null,5,null,"停炉",1.64]
["2018-04-01","检测日期","2018-04-24",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"标准（%）",null,"检测结果（%）"]
[{"$nulls":5},"1#","2#"]
[null,"热酌减率",null,5,null,2.21,"停炉"]
["2018-05-01","检测日期","2018-05-18",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"标准（%）",null,"检测结果（%）"]
[{"$nulls":5},"1#","2#"]
[null,"热酌减率",null,5,null,"停炉",1.15]
["2018-06-01","检测日期","2018-06-26",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"标准（%）",null,"检测结果（%）"]
[{"$nulls":5},"1#","2#"]
[null,"热酌减率",null,5,null,0.77,0.89]
["2018-07-01","检测日期","2018-07-08",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"标准（%）",null,"检测结果（%）"]
[{"$nulls":5},"1#","2#"]
[null,"热酌减率",null,5,null,1.4,1.94]
["2018-08-01","检测日期","2018-08-20",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"标准（%）",null,"检测结果（%）"]
[{"$nulls":5},"1#","2#"]
[null,"热酌减率",null,5,null,"停炉",0.7]
["2018-09-01","检测日期","2018-09-28",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"标准（%）",null,"检测结果（%）"]
[{"$nulls":5},"1#","2#"]
[null,"热酌减率",null,5,null,0.7,"停炉"]
["2018-10-01","检测日期","2018-10-25",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"标准（%）",null,"检测结果（%）"]
[{"$nulls":5},"1#","2#"]
[null,"热酌减率",null,5,null,0.19,0.46]
["2018-11-01","检测日期","2018-11-24",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"标准（%）",null,"检测结果（%）"]
[{"$nulls":5},"1#","2#"]
[null,"热酌减率",null,5,null,0.89,0.53]
["2018-12-01","检测日期","2018-12-07",null,"检测单位","大连华信理化检测中心有限公司"]
[null,"检测项目",null,"标准（%）",null,"检测结果（%）"]
[{"$nulls":5},"1#","2#"]
[null,"热酌减率",null,5,null,0.88,"停炉"]

{"sheet":"二噁英数据汇总","index":7,"n_rows":8,"n_cols":7,"rows_kept":8,"merged":[[0,0,0,6],[1,0,7,0],[1,2,1,3],[1,5,1,6],[2,1,3,2],[2,3,3,4],[2,5,2,6],[4,1,6,2],[4,3,6,4],[7,1,7,4]]}
["延吉天楹环保能源有限公司烟气二噁英检测数据汇总"]
["2018年   ","检测日期","2018年6月28",null,"检测单位","四川中晟环保科技有限公司"]
[null,"检测项目",null,"标准（ng-TEQ/m3）",null,"检测结果（ng-TEQ/m3）"]
[{"$nulls":5},"1#","2#"]
[null,"烟气二噁英",null,0.1,null,0.041,0.042]
[{"$nulls":5},0.023,0.028]
[{"$nulls":5},0.021,0.025]
[null,"平均值",{"$nulls":3},0.028,0.032]